## Cover Page 1
TANAMI EXPANSION 2 (TE 2)
SC6 - WALL THICKNESS
CALCULATION
DOCUMENT NO: TE2-00000-50CA-S4081-000023
VENDOR DOCUMENT NO:
PACKAGE NO:
| Rev | Date | Description | Initiated | Checked | Approved
| A | 26/02/2020 | Issued for Internal Review | L Scott | R Kanyika | K Wiehl
| 0 | 03/03/2020 | Issued for Use | L Scott | R Kanyika | K Wiehl
| 1 | 06/05/2020 | Re-issued for Use | L Scott | R Kanyika | K Wiehl

## Cover Page 2
TANAMI EXPANSION 2 (TE 2)
SC6 - WALL THICKNESS
CALCULATION
REVISION CONTROL
Revision Number | Purpose / Change | Author | Date
A | Issued for Internal Review | L Scott | 26/02/2020
0 | Update Internal Review Comments and Issued for Use | L Scott | 03/03/2020
1 | Alignment Change CS3M to SC6 and Re-issued for Use | L Scott | 06/05/2020

## SC6 Wall Thickness
TANAMI EXPANSION 2 (TE 2)
SC6 - WALL THICKNESS
CALCULATION
SC6 - WALL THICKNESS CALCULATION
1) | Determining Hazard Levels
formula:
Hazard Level Value
| H | = | PDFcFfFs
[5 empty] | Line Size | 15 | 20 | 25 | 40 | 50 | 65 | 80 | 100 | 150
| where: |  |  | unit: |  | Inputs:
| P | = | Design Pressure | MPa |  | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366
| D | = | Nominal Size | mm |  | 15 | 20 | 25 | 40 | 50 | 65 | 80 | 100 | 150
| Fc | = | Compressibility and Mass Factor (1 for Liquids) |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Ff | = | Contents Factor (10 for very harmfull liquids) |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Fs | = | Location or Service Factor (1.5 for Piping on Major Hazard facility) |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Outputs:
| H | = | Hazard Level (AS 4343) | MPa |  | 189.8235 | 253.098 | 316.3725 | 506.196 | 632.745 | 822.5685 | 1012.392 | 1265.49 | 1898.235
|  | = | Hazard Level (AS 4343 Table 2.1) |  |  | E | E | D | D | D | D | C | C | C
2) | Static Water Pressure in System
formula:
Internal Design Static Pressure
| Pr | = | ρgh
[5 empty] | Line Size | 15 | 20 | 25 | 40 | 50 | 65 | 80 | 100 | 150
| where: |  |  | unit: |  | Inputs:
| ρ | = | Rho - Density of Fluid (fluid density as determined by Process Eng group) | kg/m³ |  | 860 | 860 | 860 | 860 | 860 | 860 | 860 | 860 | 860
| g | = | Gravitational Force | m/s² |  | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81
| h | = | Total Vertical length of Pipe Line | m |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Outputs:
| Pr | = | Internal design static pressure | Pa |  | 843660 | 843660 | 843660 | 843660 | 843660 | 843660 | 843660 | 843660 | 843660
| Pr | = | Internal design static pressure | MPa |  | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366
3) | Pressure design wall thickness for static pressure
formula:
Pressure design wall thickness
| tf | = | pD / 2feMW + p
[5 empty] | Line Size | 15 | 20 | 25 | 40 | 50 | 65 | 80 | 100 | 150
where:
|  |  |  | unit: |  | Inputs:
| p | = | Internal design gauge pressure | MPa |  | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366 | 0.84366
| D | = | Outside dia of pipe as listed in tables of standards | mm |  | 21.34 | 26.67 | 33.4 | 48.26 | 60.32 | 73.02 | 88.9 | 114.3 | 168.3
| f | = | Material Design Strength (AS4041 Appendix D) | MPa |  | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138
| e | = | Weld Joint factor (AS4041 Table 3.12.2 or D12) | factor |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| M | = | Class Design Factor (AS4041 Table 3.12.3) | factor |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| W | = | Weld joint strength reduction factor (AS4041 Table 3.12.5) | factor |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Outputs:
| tf | = | Pressure Design wall thickness | mm |  | 0.065032 | 0.081275 | 0.10178 | 0.14707 | 0.18382 | 0.22252 | 0.27092 | 0.34832 | 0.51288
4) | Required wall thickness for static pressure
formula:
Required wall thickness for static pressure
| tm | = | tf + G
Nominal wall thickness
| tn | = | tm + tolerance ; 12.5% of tn
[5 empty] | Line Size | 15 | 20 | 25 | 40 | 50 | 65 | 80 | 100 | 150
where:
|  |  |  | unit: |  | Inputs:
| tf | = | Minimum required wall thickness | mm |  | 0.065032 | 0.081275 | 0.10178 | 0.14707 | 0.18382 | 0.22252 | 0.27092 | 0.34832 | 0.51288
| G | = | Corrosion & erosion allowance | mm |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Manufacturing Tolerance | % |  | 12.5% | 12.5% | 12.5% | 12.5% | 12.5% | 12.5% | 12.5% | 12.5% | 12.5%
Outputs:
| tm | = | Required wall thickness (tf + G) | mm |  | 2.065 | 2.0813 | 2.1018 | 2.1471 | 2.1838 | 2.2225 | 2.2709 | 2.3483 | 2.5129
| tn | = | Nominal wall thickness (tm + tol ; 12.5% of tn) | mm |  | 2.36 | 2.3786 | 2.402 | 2.4538 | 2.4958 | 2.54 | 2.5953 | 2.6838 | 2.8719
|  |  | Next standard manufacturers wall thickness available | mm |  | 2.77 | 2.87 | 2.77 | 2.77 | 2.77 | 3.05 | 3.05 | 3.05 | 3.4
[5 empty] | Material Grade Selected | Sch 40 | Sch 40 | Sch 10S | Sch 10S | Sch 10S | Sch 10S | Sch 10S | Sch 10S | Sch 10S