## Sheet1
Simplified Tank Overflow Calculation
Rev A
Introduction
The purpose of an overflow nozzle is to prevent the tank from exceeding its maximum allowable working pressure. This is achieved by ensuring that the simultaneous inflows can be removed via the overflow nozzle. The overflow diameter needs to be sized to enable this flow rate using the head available to it. The head is developed by the liquid level above the overflow nozzle. In a simple situation, there are two approaches. The first is to assume gravity drainage based on full flow through the nozzle. Where vibration (or unstable flow) is a risk that needs to be managed, single phase criteria should be adopted to ensure that there is sufficient head/diameter to avoid entrainment. Where it is not critical to satisfy this criteria a smaller, cheaper overflow can be specified. In the second method a more stringent criteria is used to indicate whether the vertical overflow pipe will be self venting, which eliminates the risk of unstable flow accompanied by entrained gas. For further information refer to Hills, P. D. (1983). Designing piping for gravity flow. Chemical Engineering, 90(18), 111-114.
Parameter | Symbol | Value | Units | Equation | Notes | References | Calculator notes
Proposed pipe size | D | DN250 | - |  |  |  | Input (from drop down menu)
Wall thickness | w_t | 9.27 | mm |  |  | ASME B36.10 | Automatically provided - look up and select wall thickness that corresponds to pipe size (standard weight). Can hide
Inside diameter of the pipe | d | 0.25456 | m | d = (OD - 2*w_t)/1000 | DN250 |  | Can hide
Acceleration due to gravity | g | 9.81 | m/s^2 |  | Gravitational constant |  | Can hide
Required volumetric overflow rate | Q_L | 210 | m^3/h |  | Sum of simultaneous inflows |  | Ideally would allow selection of input units
Required volumetric overflow rate | Q_L | 0.058333 | m^3/s | Q_L = Q_L /(60*60) |  | Raw water pump supply | Unit conversion, can hide
Liquid level above overflow nozzle | h | 0.27272 |  |  | Midpoint of overflow
Density | ρ | 1010 | kg/m3
Superficial volumetric flux | J_L^* | 0.7253 | - | J_L^* = (4*Q_L)/(pi()*(d^2)*(g*d)^0.5) |  | Eq 1, Hill | Need to show result
Method 1 - Flooded flow
Cross sectional area required | A_req | 0.025218 | m2 | A_req = Q_L/((2*g*h)^0.5) |  |  | Can hide
Pipe size required | d_req | 0.17919 | m | d_req = 2*(A_req/pi())^0.5 |  |  | Can hide
Pipe size required | D_flooded |  | DN |  |  |  | Look up and select nearest standard pipe size (round up)
Criteria for flooded flow
Required head | h | 0.066992 | m | h > 0.811*(Q_L^2)/(g*d^4) |  | Eq 3, Hill | Need to show result
Is sufficient head available? | - | Yes | Y / N |  |  |  | Need to show result - can be a warning if relevant
Required superficial volumetric flux | J_L^* | 1.4638 | - | J_L^* < (2*h/d)^0.5 |  | Eq 3, Hill | Can hide
Is flux criteria satisfied? | - | Yes | Y / N
Is flooded flow criteria satisfied? | - |  | Y / N |  |  |  | If E23 and E25 are "Yes" then return "Yes"
Method 2 - Unflooded (self-venting) piping
Required internal diameter | d | 0.36237 |  | d > ((4*Q_L)/(0.3*pi()*g^0.5))^0.4 | Vertical pipe only | Eq 4, Hill | Can hide
Required pipe size | D_selfventing |  | DN |  |  |  | Look up and select nearest standard pipe size (assuming standard weight wall thickness)
Is diameter criteria satisfied | - | No |  |  |  |  | Can show as a warning result, if relevant
Superficial volumetric flux threshold |  | 0.3 |  | J_L* < 0.3 |  |  | Can hide
Is flux criteria satisfied? |  | No

## Graph
see what flow could be achieved with larger (or smaller) pipe. It would be max Q_L
Flowrate
Q_L
Diameter
D

## Table
onesteel-metalcentre-pipe-and-fittings-data-charts.pdf (libertygfg.com)